Exhibit 10.1

KALLO Inc.

STRATEGIC ALLIANCE AGREEMENT

MOBILECARE

KALLO - MOBILECARE

STRATEGIC ALLIANCE AGREEMENT - MOBILE CARE

This Agreement is made by and between:

KALLO Inc.

With principal offices at 15 Allstate Parkway, Suite 600, Markham, ON L3R 5B4., Canada (“KALLO”)

AND

Petro data Management Services Limited.,

With principal offices at Motorways Center, Block-B, 1 Motorways Avenue Alausa, Ikeja, Lagos, Nigeria (“PDMS”)

AND

Gateway Global Fabrication Ltd.,

With principal offices at No-2 Olodu Street, Off Oluobasanjo Road, Portharcourt, Rivers state, Nigeria. (“Gateway”) As of the date set forth below.

Whereas, Kallo is the developer, owner and licensor of certain Mobile Care Suite of Products packages designated as the subject matter of this Agreement:

Whereas, PDMS and Gateway (Agent) desires to become a business associate of Kallo for the region of Nigeria, under the terms and conditions hereof;

Now therefore, all the parties agree as follows:

1.DEFINITIONS

For the purposes of this Agreement, the following definitions will apply:
“Business Associate” means the Kallo Authorized Agent who could be an individual, organization, or company that desires to represent the Kallo Mobile care suite of products of Kallo Inc., to the end user (customer) market. The Business Associate as it will be defined in this agreement sells the Kallo Mobile care product suite only. Kallo will be fully responsible for the training and implementation of the client

Page 2

KALLO - MOBILECARE

following the sale directly by Kallo Inc., or through it’s wholly owned Canadian subsidiary, Kallo Technologies Inc.,

“KALLO” means Kallo Inc. and/or its wholly owned subsidiary Kallo Technologies Inc.,

“Customer” means the end user of the Kallo Mobile care suite of Products that enters into the Kallo Mobile care Suite of Products End User License Agreement (EULA).

“ScheduleA” means the Kallo supplied executable pricing proposal form which must accompany any EULA for the Kallo Mobile care suite of Products in order to be accepted by Kallo.

“Kallo Mobile care suite of Products” means Kallo products as specified in Schedule A.

“EULA” means the license agreement (headed “End User License Agreement”)  between the Customer (end-user) and Kallo that sets forth the terms and conditions governing the Customer’s use of the Kallo Mobile care suite of Products.

“BookofBusiness” means the sales made by the Agent with the flow of income from those sales paid under this Agreement, all of which belongs to the Agent in right, title and interest. The Book of Business is that portion of each sale belonging to the Agent under the commission percentage agreed to at the time of sale and the continuing flow of income produced so long as the customers pay to use the Kallo Mobile care suite of products license.

"Material Breach" means the violation of the payment terms herein, copyright or trademarks, an attempt to replace or abet others to replace Kallo Mobile care suite of products or services at any existing or potential customer with competing products and any act of malicious conduct by the Agent to disparage Kallo without any justification and malicious conduct against Agent by Kallo.

"Non Material Breach" means serious neglect of Agent’s customers by the Agent in regards to support and services and any other breach of the terms of this agreement for which the cure of such shall be completed by the Agent within sixty days from written notice of violation.

"Certified Sales Agent"means a Sales Agent who has completed the initial Sales and Technical Training program and any consecutive

Page 3

KALLO - MOBILECARE

training program provided and mandated by Kallo and who abides by the terms and conditions of the certification program as outlined herein.

2.KALLO SALES AGENT PROGRAM TERMS AND CONDITIONS

a)Appointment: Kallo hereby conditionally appoints Agent as a Sales Agent, and Agent accepts in accordance with 	the provisions of this Agreement the terms of the Kallo Sales Agent Program.

b)Responsibilities: Responsibilities of the Agent (PDMS and Gateway) are defined in Schedule C. Failure to comply with this will be considered a material breach of this agreement. This also includes responsibilities for Kallo and the project management entity (BASCIC)appointed jointly by Kallo and the Agent.

c)Certified Sales Agent: Agent accepts and acknowledges that the Kallo 3 day Sales and 5 day Technical Training Program is required to be completed by the Agent within 90 days of execution of this agreement. Agent is required to pay a Training program fee of $10,000.00 for the Kallo Mobile care suite of Products on or before the date of execution of this agreement for the Authorization of Agent under this agreement by Kallo. Agent shall pay $1000/-per day for any additional days of training requested by Agent and all travel expenses plus per diem for the Kallo representative instructing the program will be due and payable to Kallo on or before execution of this agreement. Certification is mandatory for Agent to become certified to represent the Kallo Mobile care suite of products licensed under this agreement and to benefit from commissions allocated to Agent as outlined in Schedule A of this agreement. Non-compliance of this Section (2), subparagraph (c) on the part of the Agent will automatically void this agreement.

d)All sales made by the Agent of the Kallo Mobile care suite of products shall create a Book of Business owned by the Agent, which constitutes all funds due to Agent under this agreement flowing from each sale for a period not to exceed 36 months from the date of acceptance by Kallo of the Client EULA or until the EULA terminates under the provision that are outlined therein of the Kallo Mobile care suite of products.

e)Agent is required bi-monthly to report all prospects, sales activity, activity reported on Kallo provided leads, and any 	current client

Page 4

KALLO - MOBILECARE

accounts relating to the Kallo Mobile care suite of products to the Kallo Sales and Marketing department in an electronic format following the execution of this agreement. Kallo offers and enforces lead and current account protection for Sales Agents. Kallo shall not allow another Agent to solicit the existing Agents book of business unless it is understood by all parties the end user client desires the transfer. Kallo shall use its best reasonable efforts to protect the Agent from aggressive solicitation by another Agent taking any part of the Agent's book of Business. The report MUST include the Business Name, Key Contact name, telephone number, and address.

f)Exclusivity of territory (Nigeria): Agent’s appointment shall be exclusive for the Kallo Mobile care suite of products and services marked in Schedule A to this Agreement. Such appointment constitutes a grant of specific territory of Nigeria. Exclusivity is granted for the region of Nigeria, The Agent is expected to confirm the first purchase order as per Schedule D with the down payment within thee (3) months of execution of this agreement and in order to retain the exclusivity of the territory the Agent shall achieve the target commitment in Schedule D.

g)Agent shall be supplied with marketing material at no cost to agent in electronic format only. Print and mail expense are the responsibility of the Agent. Web design services, press release services, trade show design services, marketing content services, and listing services are provided at no cost to Agent as it relates to the Kallo Mobile care suite of products

h)Marketing and Sales Plan: The Agent shall prior to the signing of this agreement submit and have approved by Kallo a Marketing and Sales Plan for no less than 3 years committing the sale of no less than 15 Mobile Medical Clinics, 5 Mobile Clinics in twelve month period following the signing of this agreement as referred to in Schedule D, with minimum growth per annum thereafter of 20% cumulative. Failure to do this will be considered a material breach of this agreement.

i)Kallo shall not change the marketing and sales plan during this agreement without first discussing it with Agent and in the event that mutual agreement cannot be reached will provide at least 12 months' notice of any such change. Should agreement not be reached, Agent may maintain its existing "book of business" and cease making sales under this agreement without prejudice so

Page 5

KALLO - MOBILECARE

long as Agent meets its support obligations to its clients and financial obligations to Kallo.

j)Competence: Agent agrees to comply in full with Section (2). Subparagraph (c) of this agreement and provide and acquire appropriate staffing, training and any other requirements for the marketing, and sales of the Kallo Mobile care suite of products, and to comply with the Kallo training, support, shipping and payment terms.

k)Conduct: Agent shall undertake no acts injurious to the business or goodwill of Kallo. Agent shall use its best efforts to promote Kallo and its products and service and shall promptly report and follow up all leads provided. Agent may not offer or promote competitive products without the consent of Kallo.

l)Independent Entities: Notwithstanding the use of the designation "Sales Agent". Agent is an independent 	contractor and shall at no time have the power 
				i.to bind Kallo; 
			ii.to alter or change any terms, conditions, warranties or covenants made by Kallo or 
		iii.to create in favor of any person any rights, which Kallo has not previously agreed in writing.

m)Form of Relationship: The relationship under this Agreement shall not create any legal partnership, franchise relationship, agency or other form of legal association between the parties, which would impose a liability of one party upon the other.

n)Insurance: Agent or its successors shall maintain during the term of this Agreement and while it is still responsible 	for its Book of Business: 
			i.All required workers' compensation or similar insurance; 
		ii.Comprehensive general liability insurance. Agent shall promptly supply Kallo with proof of such insurance 			upon request. Kallo shall maintain comprehensive general liability and errors and omissions insurance for the 			Kallo Mobile care suite of products. Kallo shall promptly supply Agent with proof of such insurance upon 			request.

o)Records: Agent shall supply to Kallo the full business data of each customer as a qualified prospect and at the time 	of sale and shall, during this Agreement and while it is still responsible for its

Page 6

KALLO - MOBILECARE

Book of Business, and for a period of one year after the termination of this Agreement maintain records sufficient for Kallo to verify amounts due under this Agreement relating to the contracts, invoices, accounts, complaints, and other transactions relating to the placement and licensing of the Kallo Mobile care suite of products. Kallo may directly, or through its Agent at any time during normal business hours, upon no less than 10 business days' notice, and for any reason inspect such records and other financial information relevant to Kallo Mobile care suite of products as sold by Agent to its end users, solely for the purpose of verifying amounts due under this Agreement. Any such information will be confidential information of Agent subject to the provisions of Section 4.

p)Sub-Agents: Agent shall not be permitted to establish sub-Agents without the express written consent of Kallo.

q)Corrupt Practices: Agent represents that it will not make any payment or transfer anything of value, directly or indirectly, to any government official or employee; to any officer, director, employee, or representative, or Agent of any actual or potential customer; or to any other person or entity if such payments would violate applicable laws.

r)Prospects: Agent will provide Kallo with a list of active prospects on a regular basis as outlined in Section (2) Subparagraph (e) of this agreement. Kallo will use its best efforts to protect these prospects from being solicited by its other Agents or distributors, and to refrain from solicitation directly by Kallo, while taking into account prospect's wishes, and in as much as allowed by applicable laws. Agent in return agrees to respect active prospect lists of Kallo’s other Agents. For the above purposes, the Agent at least once every six (6) weeks and where details of each such contact are logged with Kallo define an active prospect as a prospect that is contacted.

3.WARRANTY AND LIMITATIONS

Warranties: 
	a)Kallo represents and warrants to Agent that; 
			i.it has sufficient right, title and interest in and to the Kallo Mobile care suite of products to enter into this 			Agreement; and 
		ii.all Kallo Mobile care suite of products distributed to Agent is free and clear of all liens.

Page 7

KALLO - MOBILECARE

b)Kallo Mobile care suite of products’ Warranties Agent's exclusive warranty regarding the Kallo Mobile care suite of 	products is set forth in the applicable EULA provided with the Kallo Mobile care suite of products.

Limitation of Warranties:

c)Except as stated above, Kallo makes no other warranties regarding the Kallo mobile care suite of products and documentation, and any services provided by Kallo including, without limitation, express or implied warranties, and expressly disclaims the warranties of fitness for a particular purpose or merchantability, and any other warranty, express or implied.

d)In no event shall Kallo be liable for indirect, consequential, or incidental damages (including damages for loss of business profits, business interruption, loss of business information, and the like) arising out of the relationship between Kallo and Agent even if it has been advised of the possibility of such damages.

e)Kallo's cumulative liability under this agreement, including any cause of action in contract, tort or strict liability, shall be limited to the license fees paid by agent during the 12 months prior to such event. Kallo's limitation of liability is cumulative with all Kallo’s expenditures to address liability being aggregated to determine satisfaction of the limit. Agent releases Kallo from all obligations, liabilities, claims or demands in excess of the limitation. The parties acknowledge that other parts of this agreement rely upon the inclusion of this section and the resulting allocation of risks.

f)AgentActions: Kallo shall have no obligation to any party under any warranty given by Agent, its Agents or employees. Agent shall not make any representation or warranty with respect to the Kallo Mobile care suite of products other than those stated by Kallo in its written warranty, documentation and literature.

g)AgentIndemnification: Agent agrees to indemnify Kallo and to hold it harmless from and against any loss, damage, claims or demands whatsoever arising out of Agent's activities that are outside the scope of the EULA provided by Kallo to the end user regarding use of Kallo Mobile care suite of products. Kallo makes its representations and warrants to the end user and limits

Page 8

KALLO - MOBILECARE

of liability therein via the EULA.

h)Complaints: Agent shall make all reasonable efforts to handle all incidents of customer complaints or demands 	regarding the Kallo Mobile care suite of products and shall report promptly to Kallo all such incidents.

i)Kallo indemnification: Kallo agrees to indemnify Agent and to hold it harmless from and against any loss, damage, 	claims or demands whatsoever arising out of: 
			i.Intellectual property infringement arising from the Kallo Suite of Products; 
		ii.Breach of implied warranty or negligence.

iii.Activities that are outside the scope of the EULA provided by Kallo and issued to the customer through Agent regarding the use of the Kallo Mobile care suite of products. Kallo further agrees to indemnify AGENT and to hold it harmless from and against any loss, damage, claims, or demands whatsoever arising out of Kallo's activities that are outside the scope of this Agreement.

4.CONFIDENTIALITY

Each party agrees not to disclose any confidential information received from the other in any form to any employees who do not have a specific need to use such information or to any outside party (including contractors) without the other party's prior written consent. All employees or contractors who receive such confidential information must be bound by written agreement not to disclose such information to any other party.

Each party acknowledges that the unauthorized disclosure or use of confidential information of the other party would cause irreparable harm and significant injury to the other party that may be difficult to compensate. Accordingly, each party agrees that the other party will have the right to seek and obtain temporary and permanent injunctive relief in addition to any other rights and remedies it may have. The obligations of confidentiality shall not apply to information which; 
				i.is in public domain at the time of disclosure, 
			ii.has been released by the other party without restrictions, 
		iii.has been lawfully obtained by the disclosing party from a third party under no obligation of confidentiality, or 	iv.is independently developed by employees of the disclosing party without access to the confidential 				information.

Page 9

KALLO - MOBILECARE

5.TRADEMARKS

a)Definition: "Trademarks" means any and all current or future company names, product names, marks, logos, designs, trade dress and other designations or brands used by Kallo in connection with its products and services and all marks similar thereto.

b)License: Kallo grants Agent the right to use the Trademarks solely for the purpose of distributing and marketing the 			Kallo Mobile care suite of products provided that Agent: 
i.uses the appropriate Trademarks for the corresponding Kallo Mobile care suite of products; 
ii.Identifies all Trademarks are registered trademarks of Kallo; 
iii.take reasonable steps to modify all objectionable uses of the Trademarks.

Kallo reserves the right to revoke or limit the use of Trademarks at any time upon reasonable notice. Non-Compliance with Trademark and Logo Policies shall be considered a material breach of this Agreement.

c)Ownership: Agent acknowledges that Kallo is the sole owner of the Trademarks and nothing herein shall grant to Agent any right or interest in the Trademarks. Agent shall not register, or attempt to register, any Trademarks or any marks confusingly similar thereto in any jurisdiction.

d)Limitations: Except as stated above, Agent is granted no right, title, license or interest in the Trademarks. Agent acknowledges Kallo’s rights in the Trademarks and agrees that any and all use of Trademarks by Agent shall inure to the sole benefit of Kallo. Agent agrees that it shall take no action inconsistent with Kallo ownership of the Trademarks and agrees not to challenge Kallo’s rights in or attempt to register any of the Trademarks, or any other name or mark owned or used by Kallo or any mark confusingly similar thereto.

If at any time Agent acquires any rights in, or any registration or application for, any of the Trademarks by operation of law or otherwise, it will immediately, upon request by Kallo and at no expense to Kallo, assign such rights, registrations, or applications to Kallo, along with any and all associated goodwill.

e)Notification: Agent shall promptly notify Kallo of any use by any third party of Trademarks or any use by such third 	parties of

Page 10

KALLO - MOBILECARE

similar marks which may constitute an infringement or passing off of Trademarks. Kallo reserves the right, in its sole discretion, to institute any proceedings against such third party infringers and Agent shall refrain from doing so itself. Agent agrees to cooperate fully with Kallo in any action taken by Kallo against such third parties, provided that all expenses of such action shall be borne by Kallo and all damages which may be awarded or agreed upon in settlement of such action shall accrue to Kallo. Refer to Schedule B for available means of communication to all parties concerned.

f)Co-Branding: Kallo agrees for co-branding needs with local government and sponsors logo. This is subject to: i.The submission to and approval by Kallo of the recommended Logo IProduct Name. This is to ensure that the overall look and feel of the Kallo Mobile care product is maintained.

ii.The supply of the Logo IProduct Name in suitable high quality format allowing sufficient time as defined by Kallo to incorporate co-branding logo on the Mobile clinics.

iii.Kallo agreeing to this will, in no way reduce, undermine, alter or limit their rights as outlined in section 5 and 6 of this 	agreement.

6.PROPRIETARY RIGHTS

a)Ownership: Agent understands and agrees that Agent takes title only to the media on which the Kallo Mobile care suite of products is provided. Title in and ownership of all copies of Kallo products and documentation, Trademarks and all property rights therein, shall remain at all times vested in Kallo. Agent acknowledges that the Kallo Mobile care suite of products is protected by domestic and international copyright and other forms of proprietary rights and agrees not to copy or otherwise reproduce (except as required for distribution to customers), modify, adapt, translate, reverse engineer, decompile, disassemble or create derivative works based on the Kallo Mobile care suite of products or the documentation.

b)No Rights Granted: No provision in this Agreement shall be interpreted as an assignment or grant to Agent of any 	right, title or interest in the Kallo Mobile care suite of products, documentation or Trademarks.

c)Protection: Agent agrees to take any reasonable step necessary to protect the proprietary rights of Kallo and its

Page 11

KALLO - MOBILECARE

suppliers or licensors, including, but not limited to, the proper display of copyright, trademark, trade secret and other proprietary notices on any copies of the Kallo Mobile care suite of products. Agent must reproduce and include any such notices, other legends and logos on any backup copies.

d)Copyright Notice: Agent agrees not to remove and shall reproduce and include all copyright notices or confidential 	or proprietary legends in and on all copies of Kallo Mobile care suite of products or documentation.

Any printed reference to Kallo products must include the following notice (or such notice as required by Kallo) with:
© Kallo Inc., [YEAR]. All Rights Reserved.

e)Breach: Agent understands and agrees that the protection of Kallo rights in and to the Kallo Mobile care suite of products, documentation and Trademarks and the prevention of any unauthorized copying, reproduction, modification, adaptation, translation, reverse engineering, de-compilation, disassembly and creation of derivative works, is of the essence of this Agreement and that any failure on its part, however minor, to discharge its obligations shall constitute a material breach of this Agreement.

7.TERM AND TERMINATION

a)Term: This Agreement shall enter into effect on the date it is signed by both parties as shown below.

b)Termination: This agreement shall terminate:

i.upon notification of a Material Breach that is not cured within 10 business days thereafter; 
ii.Failure to cure a non-material breach within sixty days of written notice; 
iii.Automatically, unless otherwise agreed between parties, in the event that Agent is the subject of a 		proceeding in bankruptcy which is not dismissed within 60 days, is placed in receivership, or makes an 		assignment for the benefit of its creditors; or by 
iv.Termination for "Cause" by giving 3 months written notice by the Agent or Kallo. If given by Kallo, "Cause" 		shall be defined as non-performance on the part of the Agent by failing to make sufficient efforts to market 		the Kallo Mobile care suite of products. Should the parties disagree as to what constitutes "sufficient 		marketing efforts", the issue will be submitted to binding arbitration. This course of action is not intended to 		be a means for

Page 12

KALLO - MOBILECARE

Kallo, its successors or assigns, to take over the successful operation of Agent’s business generated under this agreement without fair and just compensation.

c)On Termination: Notwithstanding any terms of this agreement to the contrary, upon termination of this Agreement for any reason whatsoever, Kallo, unless otherwise agreed, shall set aside the Agent's Book of Business to be held by Kallo.

i.The revenue stream defined by the Book of Business at the time Kallo becomes the controlling party will remain constant except in as far as any elected reduction in use by its customers. Any increase in use will not be to the benefit of the Book of Business.

ii.Kallo shall pay over all funds collected from the Book of Business and due to Agent, less a reasonable administration fee to be assessed and determined by Kallo, to Agent or its designees or assigns immediately upon receipt and act as a conduit for Agent funds, except in as far as Kallo or its assignees are required to support customers in the Book of Business in which case the cost of providing such support, will be reasonably assessed and appropriate deductions made before passing the balance to Agent. In the event Agent does not agree with the costs described in this section, the issue will be submitted to binding arbitration.

iii.Kallo shall make an accounting of funds collected to Agent or their assigns monthly. Kallo shall permit Agent or its designated Agent(s) to inspect Kallo’s books upon Agent's request at Agent's expense during normal business hours of Kallo.

iv.Kallo's failure to perform its duties in the event it becomes the controlling party of the Agent's Book of Business is a 	non-material breach of this agreement.

v.In any dispute or litigation over the terms of this agreement, the prevailing party shall have reasonable attorney fees in 	addition to any settlement or damages awarded.

d)Rights: Upon termination of this Agreement for any reason and unless otherwise agreed, all rights granted to Agent shall immediately cease and Agent shall immediately return to Kallo all Kallo Products and confidential information provided by Kallo except as otherwise provided in this Agreement.

e)No Compensation: In the event of an agreed termination of this Agreement by both parties, neither party shall be 	liable to the

Page 13

KALLO - MOBILECARE

other for damages, losses, or expenses of any kind or character on account of the termination of this agreement in accordance with its terms, whether such damage, loss, or expense may arise from the loss of prospective customers of Agent, or expenses incurred or investments made in connection with the establishment, development, or maintenance of Agent's business. Termination or expiration shall not affect any claim, demand, or liability of any party created or arising hereunder prior to such time.

8.FORCE MAJEURE

a)Definition: "Force Majeure" shall mean any event or condition not reasonably within the control of either party, which prevents in whole or in material part the performance by one of the parties of its obligations hereunder or which renders the performance of such obligations as difficult or costly as to make such performance commercially unreasonable.

b)Notice: Upon giving notice to the other party, a party affected by an event of Force Majeure shall be released without any liability on its part from the performance of itsobligations under this Agreement, except for the obligation to pay any amounts due and owing hereunder, but only to the extent and only for the period that its performance of such obligations is prevented by the event of Force Majeure. The other party may likewise suspend the performance of all or part of its obligations hereunder to the extent that such suspension is commercially reasonable. Refer to Schedule B for available means of communication to all parties concerned

9.ADDITIONAL PROVISIONS

a)Rights: Kallo grants to Agent the non-exclusive and non-transferable right to distribute the use of the Kallo Mobile care suite of products to commercial end user customers. Refer to section (2) subparagraph (f) for non-exclusive and exclusive status and qualifying requirements.

All Kallo Mobile care suite of products distributed by Agent shall be transferred solely in Kallo standard packaging and through the terms of the appropriate Kallo Mobile care suite of products EULA between the customer and Kallo provided by Kallo from time to time. Delivery of copies of the Kallo Mobile care suite of products to Agent is made solely to enable Agent to exercise this right. Agent shall not license or transfer any Kallo product for the purpose of retransfer by or to others.

Page 14

KALLO - MOBILECARE

b)Limitations: Agent shall distribute only Kallo Mobile care suite of products that Agent has obtained from Kallo and not from any other seller of the Kallo Mobile care suite of products. For Tax reasons such distribution is deemed to take place at the Agent’s business location identified above.

c)Pricing: The pricing given in Schedule A is the transfer price from Kallo to the Agent and the Agent shall, in its discretion establish a reasonable price for each of the Kallo Mobile care suite of products EULA as per Schedule A. For Maintenance Contract pricing and details refer to Schedule A, section (9), subparagraph (B). Kallo reserves the right to revise and republish prices as shown in Schedule A from time to time.

d)Payment terms: For each Kallo Mobile care suite of products license ordered by Agent from Kallo, Agent shall pay to Kallo the transfer price set forth in Schedule A. 50% of the total amount to be paid with the signed purchase order, 35% upon shipping of the goods to the carrier at Canadian port and 15% upon completion of the installation. Upon delivery of the system the Agent is responsible for getting the signed EULA from the customer before the installation process starts.

e)Taxes: All taxes from the country of origin and destination including customs duty, withholding taxes, any other levies - international / local and freight and insurance are to the end-user or customers account. The Agent will work with Kallo to add all applicable taxes to the pricing given in Schedule A and should be paid to Kallo along with the purchase order and the 50% of the value of the total system

10.ASSIGNMENT

This Agreement is not assignable by Agent without prior written consent by Kallo. In the event Agent changes its legal structure or undergoes a substantial change in ownership of its stock or other ownership interest, Kallo shall have the option of immediate termination of this Agreement. Kallo may assign this Agreement and its interest in the Kallo Mobile care suite of products to any party without the consent of Agent. This Agreement shall inure to the benefit of any successor of Kallo and shall not be affected by any change in the ownership or control of Kallo. Agent shall re execute this agreement within 60 days of the effective date of the change in ownership or change in legal structure or change of name. "Substantial change" in ownership is defined as a change in at least 51% ownership of the Agent.

Page 15

KALLO - MOBILECARE

11.MISCELLANEOUS

a)Complete Agreement: This agreement and the provisions of the current sales agent program guidelines, as amended from time to time, constitute the entire agreement of the parties with respect to the subject matter hereof and supersede all previous agreements by and between Kallo and agent as well as all proposals, oral or written and all prior negotiations, conversations or discussions between the parties related to this agreement. Agent acknowledges that it has not been induced to enter into this agreement by any representations or statements, oral or written, not expressly contained herein.

b)Amendment: This Agreement shall not be deemed or construed to be modified, amended, rescinded, cancelled or waived, in whole or in part, except by written amendment signed by the parties hereto. Refer to Schedule B for available means of communication to all parties concerned.

c)Unenforceability: If any provision of this Agreement is held to be invalid, illegal or unenforceable, such provision shall be considered severable from this Agreement and the remaining provisions shall continue in full force and effect. The parties will replace a severed provision by a provision, which is closest to the intent of the parties.

d)Notices: Notices permitted or required to be given hereunder shall be deemed sufficient if given 
i.by registered or certified mail, postage prepaid, return receipt requested, addressed to the addresses given in schedule 	B or such other addresses as the respective parties may designate by like notice from time to time, or 
ii.by international courier, telefax to or by email, the details of which are given in Schedule B.

iii.Any notice shall be deemed effective when received by the receiving party.

e)Governing Law and Jurisdiction: The laws of the province of Ontario, Canada, govern this AGREEMENT and, in respect of any dispute, which may arise hereunder; Agent consents to the jurisdiction of the federal and provincial courts of Ontario, Canada.

f)Counterparts: This Agreement shall be executed in two or more counterparts in the English language and each 	such counterpart shall be deemed an original hereof.

Page 16

KALLO - MOBILECARE

g)Waiver: No failure by either party to take any action or assert any right hereunder shall be deemed to be a waiver 	of such right in the event of the continuation or repetition of the circumstances giving rise to such right.

h)Government: If Agent is acting on behalf of any unit or agency of the United States Government, the following 				provisions apply: 
i.any products Agent acquires under this Agreement for or on behalf of the United States Government are provided to 		the United States of America with restricted rights. Use, duplication, or disclosure by the U.S. Government is subject 		to restrictions as set forth in subparagraph (c)(l)(ii) of the Rights in Technical Data and Computer Kallo Mobile care 		suite of products clause at DFARS 252.277-7013 and paragraph (d) of the Commercial Computer Kallo Mobile care 		suite of products-Restricted Rights clause at FAR 52.227-19; 
ii.Kallo grants Agent the right to transfer Kallo Mobile care suite of products to the United States government subject 			to the following restrictions. With the exception of the Department of Defense, you will not distribute the Kallo 			Mobile care suite of products to the United States of America except: 
					a.on terms at least as restrictive as those set forth in subparagraph (c)(l)(ii) of the Rights in Technical Data and 						Computer Kallo Mobile care suite of products clause at DFARS 252.227-7013 and paragraph (d) of the 						Commercial computer Kallo Mobile care suite of products -Restricted Rights clause at FAR 52.227-19, and 					b.in compliance with particular department or agency acquisition regulations that provide Kallo protection at least 						equivalent to that provided by the above-referenced DFARS and FAR provisions.

i)Export Restrictions: Agent expressly agrees to neither directly or through third parties export nor transmit any Kallo Mobile care suite of Products to any country to which such export or transmission is restricted or prohibited by applicable regulations or statutes, or any country other than the United States of America or Canada.

j)Non-Disparagement: During the term hereof and for a period of two years thereafter, each of Agent and Kallo agrees that it will refrain from making any representation, statement, comment or any other form of communication, whether written or oral (hereinafter collectively referred to as a "Communication"), to any third party, including but not limited to the principals, customers, suppliers and competitors of the other party, which Communication reflects any opinion, judgment, observation or

Page 17

KALLO - MOBILECARE

representation of fact, which has the effect or tendency to, or could have the effect or tendency to, disparage, denigrate, criticize or otherwise reflect negatively on the other party and/or the other party's products, services, officers, directors, shareholders, employees or investors (a "Disparaging Communication"). Each party agrees that it will use all reasonable commercial efforts to prevent its employees from making any Disparaging Communications regarding the other party and/or the other party's products, services, officers, directors, shareholders, employees or investors; provided, however, that nothing in this Section (11), subparagraph (j) shall restrict or impede the exercise of any rights or remedies of a Party under this Agreement.

In Witness Whereof, the Parties hereto have executed this Agreement as of the date below. And confirm, we have read, understood and agree to the terms of the strategic alliance agreement - mobile care

Kallo Inc.

JOHN CECIL 
Signature 
			John Cecil 
Name 
Chairman & CEO 
Title

| Markham, ON | 24 OCT 2011 | Gateway Global Fabrication Ltd., AJAI KUNNATH |  |
| --- | --- | --- | --- |
| Place | Date |  |  |
| Petro data Management Services Limited BABAJIDE SOYODE |  |  |  |
| Signature Babajide Soyode |  | Signature Ajai Kunnath |  |
| Name Chairman & CEO |  | Name President & CEO |  |
| Title |  | Title |  |
| Ikeja, Lagos, Nigeria | 24 OCT 2011 | River State, Nigeria | 24 OCT 2011 |
| Place | Date | Place | Date |

Page 18

KALLO - MOBILECARE

SCHEDULE - A 
Description of Kallo Mobile care suite of products

1.Mobile Acute Care Clinic

The Kallo Mobile Medical Clinics are one of a kind in the world having all the diagnostic capability for basic to mid tier specialty medical care and these units can be used in the following areas to augment healthcare delivery services.

Places where there is no hospitals or clinics and emergency situations

The Mobile Medical Clinics can be taken by road to these areas and patients or causalities can be taken into the vehicle and treated immediately with effective and real-time consultation with specialists via satellite.

Hospitals where there is no technology available for diagnosis and treatment

The Kallo Mobile Medical Clinics can be driven to, and parked in existing hospitals and patients can get the latest in technology for diagnosis and treatment, thus many hospitals in villages and rural areas can be upgraded in their healthcare services with latest equipment for diagnosis and treatment with the specialist care through remote tele-consultation.

The Kallo Mobile Medical Clinics are designed to take comprehensive health care services (preventive, promotive and curative) to rural remote villages and will reach out to the most underprivileged but needy people across the country.

The services provided are outpatient services, Ante-natal/post-natal services, identification of difficult pregnancy and referral for institutional care, Immunization- Mother & children, Minor surgery, BP examination, X-ray, ECG, First Aid, Distribution of Iron Folic tablets, Vit-A Prophylaxis, Treatment of mal-nutrient cases, etc.

Page 19

KALLO - MOBILECARE

2.Mobile Chemotherapy Clinic

The Mobile Chemotherapy Clinic serves as an extension to the chemotherapy administration in the regional Oncology departments of the teaching / general hospitals or dedicated Cancer hospitals.

Blood work is performed the day before and a nurse is then able to contact the patient in advance to review test results and schedule treatment sessions and advise pre-treatment preparation of the patient. Chemotherapy drugs and related equipment, all individually packaged for each patient, is received from the Regional Cancer hospital command center.

Chemotherapy chair that includes a chair-side touch-screen interactive system enabling patients to call a nurse, select a book for reading from the exhaustive electronic library.

Integrative medicine services such as Reiki, acupressure, and massage therapy can be delivered chair-side by specially trained nurses on staff.

Telemedicine system to enable patients to communicate with their physicians, nurses, and healthcare professionals from other disciplines and social work.

3.Mobile Dialysis Clinic

The mobile dialysis clinic works exactly like a dialysis center.

The vehicle has the clinical, technical and support staff and is well equipped with the necessary machinery required to perform the standard procedure for dialysis.

This includes dialysis machine, recliner, power backup, and a water tank with water purified through reverse osmosis (RO) system.

It has a fully automated and remote controlled dialysis chair, which works like a dialysis bed and there is a monitor defibrillator and an artificial respirator. It also carries accessories and equipment required to tackle emergencies.

The machine and accompanying accessories can be moved into homes and patients can receive the treatment along the bedside.

Page 20

KALLO - MOBILECARE

4.Mobile HIV & Malaria Clinic

Our Mobile care is equipped with a dedicated, affordable and accurate CD4+ T-cell and CD4% enumeration in HIV monitoring and patient follow-up.

The CyFlow® Counter is a fully equipped portable and ultra compact desktop flow cytometer dedicated for routine CD4 and CD4% counting (as well as total lymphocyte and WBC counting).

Equipped with Portable and Battery-Operated Fluorescence Microscope for Malaria diagnostics and monitoring.

The Partec CyScope® is a microscope for fluorescence light detection employing incident UV light and transmitted light detection. Integrated with a CCD camera for taking images of the slide for further investigation by image analysis software.

5.Mobile Clinic Command Center

The Mobile Clinic Command Center is installed in Specialist / Teaching hospitals to provide real-time support for the Front line Medical officers and staff in the Mobile Clinics for Clinical care-plan, clinical treatment protocol, clinical diagnostic protocol and procedures to optimize the Mobile clinic function and to establish seamless continuum of care.

Each Command Center, based on the throughput of patients in the Mobile clinics can manage on an average of 4-5 Mobile clinics.

Note: 
a)Medications and medical consumables are not provided in the Mobile Medical Clinics and shall be provided at additional cost.

b)Auxiliary equipment for the Mobile Clinics:

i)Stretchers, backboards, collars, drugs, medications and other medical supplies can be provided at additional cost. ii)All medical supplies to the government shall be on a contract supply based on demand, negotiated after the principal 		purchase order is placed for the Mobile Clinic.

Page 21

KALLO - MOBILECARE

6.Training:

Paramedic staff in Kallo’s Mobile Medical Clinics are provided a high level of pre-hospital medical training involving key skills not performed by technicians, including cannulation, cardiac monitoring, intubation etc., by Kallo’s Internationally accredited doctors.

7.Specialty training:

Specialty training (Focused on providing specialty care in conjunction with Specialists at teaching hospitals or Specialist care hospitals such as Pediatrics, Cardiology, Nephrology etc.,) for Front line Medical officers and staff in the Mobile Clinic and the Command center provided at additional cost based on assessment of resources and training requirements.

8.Basic training:

Basic training for Front line Medical officers and staff is included in the cost. This training is for the duration of 1 week and can hold 10 people.

Student Material for ACLS for one student is US$80/-
(Includes quick access algorithm cards) 
Text Book for Basic Trauma and life support for one student is US$120/-
Cost of Training per any additional week of 5 days is US$ 40,000/- (For Doctors and Clinical/Biomedical Engineers travel stay and charges)

9.Maintenance:

A.Mobile Clinic and Command Center maintenance is included in the Five year Standard Mandatory Maintenance as per the Program description given in Schedule E

Page 22

KALLO - MOBILECARE

SCHEDULE - B 
Communication

KALLO 
Inc., 
Attn: 	Mr. John Cecil 
Address:15 Allstate Parkway, Suite #600 
	Markham, Ontario, L3R 5B4 
	Canada 
Telephone:+1-416-246-9997 
Fax: 	+1-905-415-0332 
Email: 	john@kalloinc.com 
	anna.s@kalloinc.com

Petro data Management Services Limited., 
Attn: 	Mr. Babajide A. Soyode 
Address:Motorways Centre Block 'B', Ground Floor 1 
	Motorways Avenue, Alausa, 
	Lagos, Nigeria.

Telephone:+234-01-2708786 
	+ Fax: 
Email: 	info@petrodata.net 
	Jide.soyode@gmail.com

Gateway Global Fabrication Ltd., 
Gateway Canada and Gateway International Inc., 
Attn: 	Mr. Ajai Kunnath 
Address:GATEWAY GLOBAL FABRICATION LTD.

No-2 Olodu Street, 
Off Oluobasanjo Road, 
Portharcourt, Rivers state, Nigeria.

Address:Gateway Canada.

147 Spring Gate Blvd., 
	Thorn hill, Ontario, L4J 2B2 
Tel: 	+1-647-288-2763 
Mobile: 	+1-647-9385471 
	+ Fax: 
Email: 	ajai.kunnath@gvcal.com

Page 23

KALLO - MOBILECARE

SCHEDULE - C 
	Roles and Responsibilities defined for Kallo’s Mobile Care operations in Nigeria under this Strategic All 			Agreement 
PETRODATA

OPERATIONS 
1.Customs clearance and delivery of Mobile Clinics.

2.Training of Client's Operations 
3.Personnel of various cadres, doctors, nurses, paramedics, drivers, and medical technicians / technologists 
4.Maintenance of medical equipment 
5.Maintenance of the automobile and the engine of the Mobile Clinic and diesel generators 
6.Procurement of communication channels such as satellite feed and high-speed internet connectivity for Command Centers 7.Provision of data acquisition and back-up storage systems 
8.Supply of all local manpower, not provided by clients 
9.Supply of residential accommodation, land transport, and general 
10.Welfare amenities to all foreign personnel 
11.Specialized IT and satellite communication support for Mobile Clinics

ADMINISTRATIVE 
1.Letters of invitation to Kallo personnel for visas 
2.Procurement of all import permits and licenses 
3.Accommodation, welfare, and security arrangements 
4.Arrangements for meetings with various organizations 
5.Local transportation and security 
6.Employment of local operational support staff, as required

KALLO INC

1.Supply of Mobile Clinics and all operating equipment and software 
2.Supply of all training personnel and materials for clinical staff (Doctors, Nurses and Front line Medical officers) and Biomedical 	Engineers and software Engineers.

3.Sourcing of backup foreign medical consultants, as required 
4.Tele-health consulting for second opinion from medical specialists from US, Canada and UK 5.Procurement of all export permits and licenses 
6.Supply of drugs/medications and spare parts during and after the warranty period.

Page 24

KALLO - MOBILECARE

GATEWAY

1.Purchasing and transportation of Mobile Clinics, operating equipment, spare parts, medical consumables, drugs/medications to 	various distribution centers in Nigeria to replenish stocks in the Mobile Clinic, from Kallo Inc. Canada.

2.Customs clearance and inland transportation 
3.Assistance with local market development and liaison with clients

BAS CONSULTANTS INTERNATIONAL CORPORATION (BASCIC) (Engr. B. A. Soyode)

1.All Parties in this agreement appoint BASCIC as Project manager without prejudice.

2.Project development, management and coordination 
3.Liaison with Governments and clients and responsible for payments to Kallo and supply chain management of Medical 	consumables and medications/drugs from Kallo.

SCHEDULE - D 
Mutually accepted Sales Target

| Mobile Clinics | Year |  | Estimated Value | Remarks |
| --- | --- | --- | --- | --- |
| 2 | Q4 | 2011 | $14.575 Million | To retain Exclusivity for Nigeria |
| 3 | Q1 - Q2 | 2012 | $21.863 Million | To retain Exclusivity for Nigeria |
| 2 | Q3 - Q4 | 2012 | $14.575 Million | To retain Exclusivity for Nigeria |
| 3 | Q1 - Q2 | 2013 | $21.863 Million | To retain Exclusivity for Nigeria |
| 2 | Q3 - Q4 | 2013 | $14.575 Million | To retain Exclusivity for Nigeria |
| 3 | Q1 - Q2 | 2014 | $21.863 Million | To retain Exclusivity for Nigeria |
| 2 | Q3 - Q4 | 2014 | $14.575 Million | To retain Exclusivity for Nigeria |
| 3 | Q1 - Q2 | 2015 | $21.863 Million | To retain Exclusivity for Nigeria |
| 2 | Q3 - Q4 | 2015 | $14.575 Million | To retain Exclusivity for Nigeria |
| 3 | Q1 - Q2 | 2016 | $21.863 Million | To retain Exclusivity for Nigeria |
| 2 | Q3 - Q4 | 2016 | $14.575 Million | To retain Exclusivity for Nigeria |

Page 25

KALLO - MOBILECARE

SCHEDULE - E

Mandatory Medical Equipment Service Program for Five-year Warranty

All equipment provided in the Mobile Clinic are covered under this program and the service provision is a very unique model, where Senior Biomedical Engineers trained and certified by the manufacturers are to perform the following services located at Kallo Headquarters, coordinate with the manufacturers and the local onsite support Biomedical Technicians and provide the following services:

1.Planned and Corrective Maintenance 
2.Calibration of Medical Equipment 
3.Patient, Staff and Environment safety 
4.Breakdown Services and Maintenance 
5.Application and operation support 
6.Risk Management 
7.Codes and Standards adherence for International compliance

1.Planned and Corrective Maintenance

This program has a set of planned routine maintenance schedule for each device of medical equipment based on the original equipment manufacturers’ recommendations, applicable codes and standards given in section 7.

2.Calibration of Medical Equipment

This program has scheduled and unscheduled calibration of the medical equipment in the Mobile Clinic. Each medical device has a scheduled calibration of certain parts critical to the functional accuracy of the equipment, which is carried out as per the original equipment manufacturers’ guidelines. The unscheduled calibration of the equipment is normally carried out if and when there is a request from the staff or doctors when they observe certain calibration errors.

3.Patient, Staff and Environment Safety

Safety of patients, staff, and environment is paramount to the success of the Mobile Care project. The Joint Commission on the Accreditation of Healthcare Organizations publishes annual lists detailing “National Patient Safety Goals”  to be implemented by healthcare organizations. Goals are developed by experts

Page 26

KALLO - MOBILECARE

in patient safety, nurses, physicians, pharmacists, risk managers, and other professionals with patient-safety experience in a variety of settings. Patient safety is among the most important goals of every healthcare provider, and participation in a variety of committees and processes concerned with patient safety provides a way for biomedical managers and clinical engineering departments to gain visibility and positively affect their workplace.

Kallo’s Patient and Operator Safety Program uses a comprehensive software where in the actual work process within the Mobile Care Clinic is monitored by the onsite Biomedical Technicians guided by the Senior Biomedical Engineers at Kallo Headquarters qualified for managing the patient, staff, and environment safety to international standards.

4.Breakdown Service and Maintenance

The program covers all equipment in the Mobile Clinic. The local onsite Biomedical technicians will be the first response team to attend to any and all breakdown calls from the Mobile Clinic. The Biomedical Technicians will then have Kallo Biomedical Engineer support to resolve the issues as quickly as possible. After the breakdown service is carried out and the equipment is fixed and recalibrated, the Senior Biomedical Engineers would then advise if a maintenance service has to be carried out to due to the nature of breakdown.

5.Application Support

The program covers all medical equipment in the Mobile Clinic. Kallos’  Certified Clinical Engineers / Biomedical Engineers and Clinical Application support specialists will be available via Video/Teleconference/Telehealth systems in the Mobile clinic for all clinical application support in using technology for diagnostic and therapeutic healthcare services. This is a critical component of the program offered in order to make it successful in using technology at the front end which is normally neglected by all medical equipment manufacturers’ when the equipment is deployed in remote areas with medical staff who are not exposed to technology as the case may be in urban areas, developed cites or countries.

6.Risk management

This program helps avoid the likelihood of equipment-related risks, minimize liability of mishaps and incidents, and stay compliant with regulatory reporting requirements.

In addition, user error, equipment abuse, no problem/fault found occurrences

Page 27

KALLO - MOBILECARE

must be tracked to assist risk management personnel in determining whether additional clinical staff training must be performed.

Risk management for IT networks incorporating medical devices will be covered by the standard ISO/IEC 80001. Its purpose is: "Recognizing that MEDICAL DEVICES are incorporated into IT-NETWORKS to achieve desirable benefits (for example, INTEROPERABILITY), this international standard defines the roles, responsibilities and activities that are necessary for RISK MANAGEMENT of IT-NETWORKS incorporating MEDICAL DEVICES to address the KEY PROPERTIES". Such as ISO 20000 in the context of medical applications, e.g. configuration, incident, problem, change and release management, and risk analysis, control and evaluation according to ISO 14971. IEC 80001 "applies to RESPONSIBLE ORGANIZATIONS, MEDICAL DEVICE manufacturers and other providers of information technologies for the purpose of comprehensive RISK MANAGEMENT".

7. Codes and Standards adherence for International compliance:

1. JCAHO Comprehensive Accreditation Manual 
2. AABB 
3. NFPA 99 
a. Gas and Vacuum Systems 
b. Electrical Systems 
4. FDA 
5. SMDA 
6. OSHA

Page 28

KALLO - MOBILECARE

SCHEDULE - F 
	Medical Equipment description 
		Blood Chemistry Analyzer 
Advanced i-STAT Cartridge Technology or equivalent system

Most Comprehensive Bedside Testing Platform:

i-STAT cartridge technology streamlines traditional lab technology, yet contains many of the components found in complex lab testing systems. Each test cartridge contains chemically sensitive biosensors on a silicon chip that are configured to perform specific tests. To perform a test, 2 to 3 drops of blood are applied to a cartridge, which is then inserted into the i-STAT handheld. Prior to running a test, each cartridge initiates a series of preset quality control diagnostics, from monitoring the quality of the sample to validating the reagent.

Each i-STAT single-use cartridge uses advanced biosensor technology that applies microfluidics to process the most comprehensive range of clinical tests in a single platform, allowing clinicians to access the time-sensitive diagnostic information they need, when and where they need it. Available tests include diagnostic indicators related to disease state and clinical practice guidelines.

Test-specific, single-use i-STAT cartridges are available for a range of clinical tests, including cardiac markers, lactate, coagulation, blood gases, chemistries and electrolytes, and hematology.

Delivers lab-quality test results to the clinician within minutes 
The portable i-STAT handheld makes patient-side testing easy:
	·requires no special sample preparation or user calibration; maintenance is minimal		·weighs 18 ounces, making it completely portable
	·features ergonomically designed soft keys for comfort and ease of use

Patient-side testing is as easy as entering the operator and patient information into the handheld, inserting one of the several testing cartridges, and then viewing test results:
		·The system prompts users step by step through the testing process
		·Operator and patient information can be entered via barcode scanner
	·Operator lockout prevents unauthorized users from performing or viewing test results

Page 29

KALLO - MOBILECARE

·Test results are uploaded automatically when the i-STAT handheld is placed in a downloader 
With over 50,000 handhelds placed in high-acuity settings worldwide-including over 1,800 hospitals-and over 35 million test cartridges produced annually, the i-STAT System is trusted to provide lab-quality results.

i-STAT Integration Into Point-of-Care Data Management and Electronic Medical Records 
The i-STAT® System can integrate test results with your Lab Information System (LIS) and Electronic Medical Records (EMR). This is achieved through flexible connectivity and interfacing solutions, which serve to ensure your facility gets real-time results in the patient electronic chart.

i-STATSystem integration with Laboratory Information Systems (LIS)/Electronic Medical Records (EMR)

The i-STAT System connects to the Point-of-Care Data Management System of your choice and then interfaces to the EMR via your LIS. Integration options include:
		·The Central Data Station System from Abbott Point of Care
	·Abbott Diabetes Care PrecisionWeb®
		·Medical Automation Systems RALS+™ RALS® Plus
		·Telcor Quick-Linc®

Addressing Documentation Challenges with STATNotes™
STATNotes is a highly customizable documentation solution for the i-STAT 1 handheld. This unique feature facilitates timely documentation of complex and critical data by prompting the user to enter information into the i-STAT 1 during the testing process. The information is then automatically uploaded to the patient chart with the test results. Customizing your i-STAT System to prompt data entry:

Page 30

KALLO - MOBILECARE

·streamlines workflow
	·helps reduce errors
	·allows for increased efficiency
	·facilitates compliance 
STATNotes can help guide users to be compliant with The Joint Commission National Patient Safety Goals and hospital policies. For example, many of our customers use STATNotes to capture comprehensive ventilator setting information, documentation of critical test notification, and “read back” acknowledgment of critical tests and critical values.

Data Management and Laboratory Regulatory Compliance 
The i-STAT System gives you control over who can use the device and access test results. It also offers many features designed to help laboratories maintain regulatory compliance, such as:
		·managing operator certification and device lockout
	·reporting on operator performance
		·reporting on both liquid and equivalent quality control
		·reporting on reagent usage
		·laboratory Information System interfacing

Abbott Point of Care will work with your team to ensure seamless integration with your data management system.

Urine Chemistry Analyzer 
		CLINITEK Status® Analyzer or equivalent system 
Intended Use
	·The Analyzer is for in vitro use in the semi-quantitative detection of albumin, bilirubin, blood (occult), creatinine, glucose, ketone 	(acetoacetic acid), leukocytes, nitrite, pH, protein, specific gravity and urobilinogen in urine samples, depending on the type of 	Siemens urinalysis strip used.

·The semi-quantitative calculation of albumin-to-creatinine and protein-to-creatinine ratios in urine samples, when Clinitek®Microalbumin and Multistix PRO® Reagent Strips for Urinalysis are used.

·The detection of human Chorionic Gonadotropin (hCG) in urine samples, when Clinitest® hCG cassettes are used.

Table of Results 
The results shown in shaded areas will be marked as positives, if "mark positive results" is selected in Instrument Set Up. The results will be marked by asterisks when displayed, when printed and when the data is transferred to a host computer.

Page 31

KALLO - MOBILECARE

Page 32

KALLO - MOBILECARE

Urinalysis has become an indispensable tool in healthcare.

·Provides important markers to detect early stages of many disease states, such as diabetes, kidney disease and urinary tract infections.

·Enhances disease monitoring and patient management.

·Semi-quantitative results have proven to be cost-effective and virtually immediate.

In today's busy physician's office environment, interruptions are frequent and can contribute to timing errors and variability in results when urinalysis strips are read visually. Studies have shown that when urinalysis is performed with an instrument, sensitivity is increased and positives are correctly identified and reported.1

1. Tighe P. Improving the quality of urine strip testing: The Clinitek 50 urine chemistry analyser. Euro Clin Lab, June 1997,16:20.

Page 33

KALLO - MOBILECARE

Page 34

KALLO - MOBILECARE

Digital Radiography System 
RadPRO D2RSDynamic Digital Remote RF System or equivalent system Digital Radiography & Fluoroscopy Solutions

Features
	•Canon CXDI-50RF Dynamic/Static Digital Radiography SystemThe RadPRO D2RS Dynamic Digital Remote RF 	System is compatible with the Canon CXDI-50RF Dynamic/Static Digital Radiography System that includes a Cesium Iodide 	scintillator. Including both dynamic and static capabilities, high resolution images are produced and may be previewed within 2-4 	seconds after exposure in the radiography mode with the optional monitor. The radiography mode produces up to 15 frames per 	second (fps), and up to 30 fps in the fluoroscopy mode, depending on the image capture mode and size. The detachable cable 	allows the digital detector to be used in multiple rooms or multiple locations within the same room.

•Dynamic and Static ImagingThe Canon CXDI Control Software RF, designed specifically for the Canon CXDI-50RF Dynamic/Static Digital Radiography System, features a wide range of fluoroscopic procedures and includes all the standard DICOM functions. Exams include spine, Osteo-articular, Barium swallow and esophagus, stomach and small intestine, Barium enema and large bowel, Endoscopy/ERCP, Urography, Cystography, Hysterosalpingography, Myelography, Arthrography, Venography and more. The software also delivers high-resolution images, generator communication for preset X-ray parameters, provides actual exposure factors and patient dose information in the DICOM header. Studies that require full spine and long leg imaging are fully automated. With the automated stitching capability up to 4 images can be stitched together.

Page 35

KALLO - MOBILECARE

•	High Quality ImagesHigh resolution static images can be previewed within 3-5 seconds after exposure on a monitor (optional). Images may be configured automatically with post-processing and are ready to be printed or transmitted through the network using industry standard DICOM protocols.

•	Full Patient CoverageEnd-to-end table coverage is available when the motorized tube column angulation is combined with the motorized tube rotation. The motorized table adjusts the height, and the low minimum height simplifies access for patients with mobility issues. When patients arrive at the radiology room on a trolley or in a bed, Smart Access provides clear access to a 47 inch (120 cm) section of the table top to allow for a simplified transfer. The table loading capacity accommodates patients weighing up to 500 lbs (230 kg).

•	Auto-PositioningTable movements, collimation and spectral filtration settings, exposure and digital acquisition parameters may be administered with the single touch, remote-controlled user-interface reducing the preparation time needed for exams.

Digital Retina Scanner 
CR-2 PLUS or equivalent system 
Digital Non-Mydriatic Retinal Cameras

Overview 
The Canon CR-2 PLUS Digital Non-Mydriatic Retinal Camera provides Color and Fundus Autofluorescence (FAF) imaging within a small compact design. Geographic Atrophy, Macular Degeneration, Glaucoma, Diabetic Retinopathy and other conditions that can affect vision may also be identified and monitored using FAF mode. Using invisible infrared alignment light, the digital non-mydriatic camera may image patients with pupils as small as 3.3 mm (small pupil mode) without dilation drops. This is especially useful when performing retinal screenings or expediting routine retinal imaging exams during office visits.

Page 36

KALLO - MOBILECARE

Features
	•Non-Mydriatic Fundus Autofluorescence (FAF) PhotographyFundus Autofluorescence (FAF) helps monitor macular 		waste (e.g. lipofuscin) which can accumulate in the Retinal Pigment Epithelial (RPE) layer. The accumulation of macular waste 		can cause conditions such as Age-Related Macular Degeneration (AMD) which can lead to reduced vision. The FAF mode 		may be selected by pressing only one button.

•Digital Filter ProcessingRed-Free and Cobalt digital filters are included and provide enhanced screening exams. Red-Free is used for evaluating the Retinal Nerve Fiber Layer (RNFL) and vascular structure of the retina associated with documenting Glaucoma, Diabetic Retinopathy or Hypertension. The Cobalt filter is also used for evaluating the RNFL, as well as Optic Disc and Optic Disc Drusen. Additionally, Green (Vascular view) and Red channel (Choroid view) digital filter views are also included.

•Compact and LightweightThe small design of the CR-2 PLUS facilitates portability when needed using an optional hard shell transport case sold separately. Canon instrument tables (sold separately) may comfortably fit both the camera and computer workstation (sold separately). The space saving design also allows for use in limited office space environments.

•Dedicated EOS Camera TechnologyHigh quality diagnostic images are obtained using a dedicated camera for the CR-2 PLUS which incorporates a large, high-definition CMOS sensor with 18 megapixels. When the camera cover is removed, the LCD may be adjusted to a variety of titled angles to suit the user's point of view.

•Low Flash Intensity and ISO SensitivityThe low flash intensity of the CR-2 PLUS minimizes miosis, thus shortening the time required for taking multiple view exams or stereo images. The reduced brightness improves patient comfort and reduces the "ghost" image the patient sees after an exposure. A wide range of low ISO speeds are supported including ISO 200, 400, 800, 1600, 3200 and 6400.

•Automatic Exposure FunctionThe CR-2 PLUS measures the volume of infrared light from the retina and automatically adjusts the flash intensity for observation and photography. This feature may be set to ON/OFF and can be adjusted using the operation panel.

•Control PanelThe simplified design of the control panel can be easily handled by an examiner. The one-handed joystick may be used to position the camera to acquire the desired image. In darkly lit rooms, the operation panel illuminates for easier navigation. The short main body of the CR-2 PLUS provides minimal distance between the patient and the operator allowing easy access to adjust the patient's position or eyelids.

•Retinal Imaging Control SoftwareUsing the Canon Retinal Imaging Control Software (RICS), images can be captured, viewed, processed, printed and saved to a permanent storage database. The Canon RICS complies with the DICOM®* Standard. Images may be stored as DICOM or JPEG files. For more information, visit Retinal Imaging Control Software.

Page 37

KALLO - MOBILECARE

Ultrasound Scanner 
LOGIQ 9 or equivalent system

E-Series transducers 
Incredible transducer technology makes imaging incredibly easy.E-Series transducers set an entirely new standard in acquiring extraordinary images. The moment you put the transducer on the patient, these highly advanced, ergonomically designed transducers work with the agile architecture to maximize image quality.

Highly advanced transducer technologies for high-quality images:·Acoustic Amplifier Technology
·Single Crystal Technology
·Matrix Array Technology
·Volume Hybrid Technology

Acoustic Amplifier Technology built into the new E-Series transducers achieves higher sensitivity by recycling the acoustic energy that used to pass through the transducer crystal. It redirects this previously wasted energy back into the piezoelectric crystal, adding significantly to the transducer sensitivity.

Page 38

KALLO - MOBILECARE

Single Crystal Technology increases bandwidth, offering better signal to noise and improved axial resolution and penetration.

Matrix Array Technology helps achieve uniform resolution throughout the field of view, eliminating the compromise between penetration and image resolution.

Volume Hybrid Technology encompasses a new range of Volume transducers bringing an outstanding spatial and temporal resolution.

LOGIQ E9 knows the next step of a scan and helps you get there like no other ultrasound system can. It’s all part of the technologically advanced Scan Assistant, your customizable scanning protocol.

Scan Assistant does things that an ultrasound system has never done before, including automatically steering color Doppler and setting up imaging controls and modes for you. Now you can truly concentrate less on keystrokes and more on patient care.

Digital Smartscope 
Optomed Smartscope or equivalent system

Optomed Smartscope is a digital camera that provides general, ophthalmoscope, otoscopic and dermatoscopic imaging with one hand -held device.

Page 39

KALLO - MOBILECARE

Multi Function Digital Stethoscope 
CMS VESD Digital Stethoscope or equivalent system

CMS-VESD is a multi-functional visual stethoscope. On the basis of stethoscope function, it is added with ECG and SpO2 monitoring function. The multi-functional characteristic of the device makes it is effective on emergency treatment.

·Compact and portable, easy to use
·Suitable for adult, pediatric and neonatal patients.

·Heart, Lung, Heart and Lung sound models for Stethoscope.

·Large color LCD display of ECG, SpO2 and Pulse rate
·Adjustable audible and visual alarms
·Real-time monitoring.24 hours storage and review of data
·SD card memory, all data can be transferred to a PC
·Low power consumption.

Specification
	·Power Supply : Lithium Battery DC3.6~DC4.2V
	·Display : 2.4" Color LCD 
Stethoscope
	·Heart：20～230Hz
	·Lung：100～800Hz
	·H& L：20～800Hz
	·Accuracy:± 2 bpm

Page 40

KALLO - MOBILECARE

Heart Rate
·Measurement range: 30bpm～300bpm;
·Accuracy: ± 2 bpm

Pulse Rate
·Measurement range: 30bpm 250bpm;
·Accuracy: ± 2 bpm or ± 2%

SpO2
·Measurement range: 35%～100%;
·Accuracy: 70~100% (± 2% ) <70% unspecified.

Patient Weighing Scale for Telehealth 
UC321 Digital Weighing scale or equivalent system

Personal Scales for Telemonitoring
·Precise measurements
·Displays weight in either pounds or kilograms
·Memory recall with time/date stamp on select models
·Includes four attachable feet for carpet use
·Motion Tolerance Mode on select models

An accurate and precise scale specifically designed for telemedicine applications.

The UC-321 series provides highly accurate and precise measurements for telemedicine applications. These scales are one of the thinnest and lightest scales on the market. Measuring less than 1” thick, it is easy to step on and store.

Page 41

KALLO - MOBILECARE

This sleek and stylish unit offers more precise readings and functionality compared to traditional scales. Available with wired or wireless communications.

Digital Blood Pressure Monitor for Telehealth 
AND Digital Blood Pressure Monitor or equivalent system

Blood Pressure Monitors for Telemonitoring
·Professional accuracy via oscillometric method
·Clinically validated
·One button operation
·Memory storage
·Provides time and date stamp
·Each monitor has unique serial number
·Meets ANSI/AAMI SP10 standards

A leading blood pressure monitoring system among telemonitoring service providers.

This blood pressure monitor can send real-time blood pressure measurements to the Access Point. These devices can also operate in a batch-mode to send a number of measurements with time and date in a single request command. Available with wired or wireless communications.

Page 42

KALLO - MOBILECARE

Telepharmacy Solution

Integrates remote or local pharmacist-controlled dispensing system cabinetry and software, pharmacy software and televideo technology into one system individually designed to meet all your needs. It brings real-time medication dispensing and pharmacist counseling to the point of care.

Improves patient care and satisfaction
·Provides immediate medication access - no more waiting or unnecessary trips.·Enhances prescription fulfillment - resulting in greater patient compliance.

·System software/multiple barcode verifications virtually eliminate dispensing errors.

Page 43

KALLO - MOBILECARE

SCHEDULE - G 
	Kallo Mobile care suite of products 
(Price is subject to change based on the requirement and configuration of various systems in the Mobile Clinic, and is exclusive of taxes, levies custom duties, freight and insurance.)

| Description | Kallo Price | Agent Markup | End user price |
| --- | --- | --- | --- |
| Mobile Acute Care Clinic - Base price | $2,650,000 | $265,000 | $2,915,000 |
| Standard Mandatory Maintenance Service for 5 years | $2,915,000 | $1,457,500 | $4,372,500 |
| Description | Kallo Price | $1,722,500 | $7,287,500 |
|  |  | Agent Markup | End user price |
| Mobile Chemotherapy Clinic - Base price | $1,850,000 | $185,000 | $2,035,000 |
| Standard Mandatory Maintenance Service for 5 years | $2,035,000 | $1,017,500 | $3,052,500 |
| Description | Kallo Price | $1,202,500 | $5,087,500 |
|  |  | Agent Markup | End user price |
| Mobile Dialysis Clinic - Base price | $1,600,000 | $160,000 | $1,760,000 |
| Standard Mandatory Maintenance Service for 5 years | $1,760,000 | $880,000 | $2,640,000 |
| Description | Kallo Price | $1,040,000 | $4,400,000 |
|  |  | Agent Markup | End user price |
| Mobile HIV & Malaria Clinic - Base price | $1,800,000 | $180,000 | $1,980,000 |
| Standard Mandatory Maintenance Service for 5 years | $1,980,000 | $990,000 | $2,970,000 |
| Description | Kallo Price | $1,170,000 | $4,950,000 |
|  |  | Agent Markup | End user price |
| Command Center for Mobile Clinics | $550,000 | $55,000 | $605,000 |
| Standard Mandatory Maintenance Service for 5 years | $605,000 | $302,500 | $907,500 |
|  |  | $357,500 | $1,512,500 |

NOTE: 
PRICING INCLUDES TELE PHARMACY SYSTEM COSTING $150,000/ - FOR EACH MOBILE CLINIC.

Page 44